|  | ......................... pcs. .............................. € .............................. € GEZE Terminal IP 54 - external application, stainless steel V2A for securing a door along escape and rescue routes in an external application, tested in accordance with EltVTR (German directive for electrical locking systems on escape route doors) and EN 13637, with no integrated control unit. Suitable for connection to GEZE door control units in bus technology. Sturdy, protected against vandalism, as well as visually high-quality version in V2A stainless steel. Equipment: • Stainless steel housing with stainless steel front plate in sabotage-protected version • Integrated SCT 222 key switch for authorised door passage Connection to GEZE door control units Bi-colour LED green/red for indication of the state unlocked/locked Yellow LED for indication of the alarm state Key switch with two-sided switching operation for unlocking and short-time release/locking Complete with Euro profile cylinder and 3 keys IP rating IP 54 Integrated NOT 220 emergency push button Illuminated emergency push button with lead-sealable reusable cover, plastic casing Illumination with long-life LED. IP rating IP 65 Functions: For this functionality, an external GEZE door control unit is needed in the protected, separated area, e.g. TZ 322 SN. For use in accordance with EN 13637, a TZ 320 door control unit has to be used. Version: ( ) Emergency push button information label ( ) Emergency push button information label FWS back in accordance with EltVTR, non-illuminated Fixed from the back on Makrolon panel, integrated in front plate ( ) Emergency push button information label in accordance with EN 13637, non-illuminated Fixed to the front plate from the front (note: an additional notice sign is required according to the EltVTR on doors with requirements under EN 13637 and the EltVTR). ( ) Surface-mounted installation: Dimensions of surface-mounted housing (W x H x D): 105 x 305 x 84 mm Dimensions of front plate: (W x H x D): 105 x 305 x 1.5 mm Housing and front plate made of V2A stainless steel ( ) Flush-mounted installation with flush-mounted box: Dimensions of UP housing: (W x H x D): 105 x 305 x 84 mm Dimensions of front plate: (W x H x D): 135 x 335 x 1.5 mm Flush-mounted box and front plate made of V2A stainless steel |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € GEZE TZ 320 door control unit in bus technology With integrated control unit, tested in accordance with EltVTR (German directive for electrical locking systems on escape route doors) and EN 13637. Equipment: • Control unit with illuminated emergency push button LED displays for the following operating states: - Door locked/unlocked/short-term released - Door open/closed - Alarm, pre-alarm, fault Coloured terminals to distinguish connections for the peripherals. Large-surface barrier-free impact cover with sabotage protection. Integrated weekly timer as well as automatic storage of the operating state and user data after power failures up to 24h. 3 programmable inputs, 2 programmable outputs • Integrated emergency push button information label, not illuminated Connections: • 3 programmable inputs for connection of timer, fire alarm system, burglar alarm system, access control, locks with cylinder contact etc. Function: High active, low active and disable can be chosen per state • 2 programmable outputs for connection of swing door drive, motor lock, lever lock, additional electric strike, visual or acoustic alarm indication etc. Function: Normally closed, normally open and disable can be chosen per state • Input for indirect activation through external emergency push buttons • Input for external key switch for control of modes of operation • Input for feedback of the door mode • Input for feedback of the locking status • Prepared for networking with GEZE Cockpit Functions: • Abort and retriggering in combination with short-term release • Combination with GEZE swing door drives possible without additional components • Control and visualisation via GEZE Cockpit and TE 220 tableau possible, and if there is a connection to GEZE Cockpit via IO 420, a transfer to a building management system is possible • Burglar alarm system and fire alarm system signals as well as timer can be forwarded via GEZE BUS to all devices in a bus line. 5 groups each are possible • Integrated interlocking door system function (active, passive and combined). 10 groups possible • Integrated buzzer for acoustic signalling during alarms and pre-alarm • Integrated weekly timer • Alarm memory with date and time • Automatic storage of operating state and user data after power failure for up to 24 doors Version: ( ) Emergency push button information label ( ) Design in accordance with EltVTR ( ) Design in accordance with EN 13637 ( ) Lighting for the integrated emergency push button information label (note: an additional notice sign is required according to the EltVTR on doors with requirements under EN 13637 and the EltVTR). ( ) Key switch with 2 switch contacts incl. Euro profile half cylinder for setting the functions short-time release, permanent unlocking, locking and alarm reset ( ) Integrated power supply Mains voltage 230 V AC, Operating voltage 24 V DC Output current max. 600 mA (with control units in accordance with EltVTR) Output current max. 650 mA (with PVC surface-mounted control units in accordance with EltVTR) Output current max. 1 A (with control units in accordance with EN 13637) ( ) Surface-mounted installation: Plastic housing, dimensions (W x H x D): 77x197x 90 mm ( ) Colour similar to RAL 6032 (green) ( ) Colour: white aluminium Stainless steel housing Housing, dimensions (W x H x D): 78 x 240 x 68.5 mm Front plate, dimensions (W x H x D): 78 x 240 x 1.5 mm ( ) Stainless steel V2A, brushed ( ) With LED backlight red/green to indicate system statuses by means of backlighting ( ) Flush-mounted installation: Switch programme, dimensions (W x H x D): Triple frame 81 x 223 x 62.5 mm ( ) AS500 in alpine white by Jung ( ) LS990 in stainless steel by Jung ( ) LS990 in alpine white by Jung ( ) E2 in pure white by Gira ( ) E2 in anthracite by Gira Stainless steel in flush-mounted box Housing, dimensions (W x H x D): 77 x 239 x 68.5 mm Front plate, dimensions (W x H x D): 98 x 260 x 1.5 mm ( ) Stainless steel, brushed ( ) With LED backlight red/green to indicate system statuses by means of backlighting Stainless steel in flush-mounted boxes Front plate, dimensions (W x H x D): 98 x 260 x 1.5 mm Spacer frame, dimensions (W x H x D): 98 x 260 x 10 mm Installation of the individual components (control unit, key switch, power supply) in deep standard flush-mounted boxes ( ) Front plate in brushed stainless steel, acrylic white spacer frame ( ) With LED backlight red/green to indicate system statuses by means of backlighting Use for doors: ( ) single leaf ( ) double leaf |
|  | ......................... pcs. .............................. € .............................. € GEZE TZ 322 door control unit in bus technology With integrated control unit. Version without emergency push button Tested in accordance with EltVTR (German directive for electrical locking systems on escape route doors) in connection with an external emergency push button (approval needed for application without local emergency push button on the door) Features: • Control unit without emergency push button LED displays for the following operating states: - Door locked/unlocked/short-term released - Door open/closed - Alarm, pre-alarm, fault Coloured terminals to distinguish connections for the peripherals. Integrated weekly timer as well as automatic storage of the operating state and user data after power failures up to 24h. 3 programmable inputs, 2 programmable outputs Connections: • 3 programmable inputs for connection of timer, fire alarm system, burglar alarm system, access control, locks with cylinder contact etc. Function: High active, low active and disable can be chosen per state • 2 programmable outputs for connection of swing door drive, motor lock, lever lock, additional electric strike, visual or acoustic alarm indication etc. Function: Normally closed, normally open and disable can be chosen per state • Input for indirect activation through external emergency push buttons • Input for external key switch for control of modes of operation • Input for feedback of the door mode • Input for feedback of the locking status • Prepared for networking with GEZE Cockpit Functions: • Abort and retriggering in combination with short-term release • Combination with GEZE swing door drives possible without additional components • Control and visualisation via GEZE Cockpit and TE 220 tableau possible, and if there is a connection to GEZE Cockpit via IO 420, a transfer to a building management system is possible • Burglar alarm system and fire alarm system signals as well as timer can be forwarded via GEZE BUS to all devices in a bus line. 5 groups each are possible • Integrated interlocking door system function (active, passive and combined). 10 groups possible • Integrated buzzer for acoustic signalling during alarms and pre-alarm • Integrated weekly timer • Alarm memory with date and time • Automatic storage of operating state and user data after power failure for up to 24 doors Version: ( ) Key switch with 2 switch contacts incl. Euro profile half cylinder for setting the functions short-time release, permanent unlocking, locking and alarm reset ( ) Integrated power supply Mains voltage 230 V AC, Operating voltage 24 V DC Output current max. 600 mA Output current max. 650 mA (with surface-mounted control units in plastic housing) ( ) Surface-mounted installation: Plastic housing, dimensions (W x H x D): 77x197x 90 mm ( ) Colour similar to RAL 6032 (green) ( ) Colour: white aluminium Stainless steel housing Housing, dimensions (W x H x D): 78 x 240 x 68.5 mm Front plate, dimensions (W x H x D): 78 x 240 x 1.5 mm ( ) Stainless steel V2A, brushed ( ) With LED backlight red/green to indicate system statuses by means of backlighting ( ) Flush-mounted installation: Switch programme, dimensions (W x H x D): Triple frame 81 x 223 x 62.5 mm ( ) AS500 in alpine white by Jung ( ) LS990 in stainless steel by Jung ( ) LS990 in alpine white by Jung ( ) E2 in pure white by Gira ( ) E2 in anthracite by Gira Stainless steel in flush-mounted box Housing, dimensions (W x H x D): 77 x 239 x 68.5 mm Front plate, dimensions (W x H x D): 98 x 260 x 1.5 mm ( ) Stainless steel, brushed ( ) With LED backlight red/green to indicate system statuses by means of backlighting Stainless steel in flush-mounted boxes Front plate, dimensions (W x H x D): 98 x 260 x 1.5 mm Spacer frame, dimensions (W x H x D): 98 x 260 x 10 mm Installation of the individual components (control unit, key switch, power supply) in deep standard flush-mounted boxes ( ) Front plate in brushed stainless steel, acrylic white spacer frame ( ) With LED backlight red/green to indicate system statuses by means of backlighting Use for doors: ( ) single leaf ( ) double leaf |
|  | ......................... pcs. .............................. € .............................. € GEZE FTV 320 escape door lock Electric locking mechanism for doors along escape and rescue routes according to the fail-safe principle. Guarantees reliable and immediate unlocking of the door, even with high latch preload. With integrated feedback contact for monitoring the door mode and locking status as well as for sabotage monitoring. High resistance against attempts to break open. Universal application: DIN right / left, horizontal / vertical, door leaf / frame. Face plate pre-mounted to locking element, strike plate can be ordered separately as counterpart. Face plate and strike plate made of corrosion-resistant stainless steel. Operating voltage: 24 V DC, Current consumption: 100 mA in locked state Current consumption: 240 mA briefly during locking Service temperature: -20 / +60 °C Suitability certificate: EltVTR (German directive for electrical locking systems on escape route doors), tested with TZ 320 in accordance with EN 13637 Resistance against breaking open: at least 5,000 N Latch preload: at least 3,000 N Clearance: 5 mm ± 2 mm Dimensions: 15.2 x 138.8 x 37.7 mm (W x H x D) Notes: 1) The escape door lock is mounted in addition to the existing panic lock. 2) The face plate design and the strike plate design must be specified at the time of placing the order/awarding the contract. |
|  | ......................... pcs. .............................. € .............................. € GEZE MA 500 holding magnet With counterplate for the magnetic locking of emergency exits. Suitability certificate: EltVTR (German directive for electrical locking systems on escape route doors), tested with TZ 320 in accordance with EN 13637 Resistant against attempts to break open 5000 N, with integrated Hall sensor for monitoring and bi-colour LED for indicating the locking status. Rated operating voltage 24 V DC, PG9 connection, current consumption 250 mA, Version: silver-coloured To be installed only using an installation set: ( ) on the hinge side ( ) on the opposite hinge side ( ) for reveal installation with reed contact: ( ) flat reed contact with ceiling mounting bracket ( ) flat reed contact with cross hole and mounting base ( ) block reed contact with mounting base for steel doors Note: The holding magnet is usually installed independent of the panic locks. |
|  | ......................... pcs. .............................. € .............................. € GEZE Cockpit building automation system compact design, for control cabinet or wall installation Key features are: High-performance embedded Linux PC Operation without fan suitable for installation in closed control cabinet housings Installation on DIN rail Connections to the device accessible from the top and bottom through perforated gaps in the housing Protection against external electric, electromagnetic and mechanical influences Supply voltage 24 V DC Optional rechargeable battery operation possible (emergency power operation) Supports the BACnet Standardized Device Profile B-BC (BACnet Building Controller) 2x RS485 interface for the connection of up to 62 IO 420 interface modules (31 IO 420 per strand) Communication with the field devices via IO 420 interface module 2x RJ45 interfaces for communication with Additional automation stations Room automation systems Control units Control and management systems PC networks Communication with other systems on the communication standard BACnet IP Automatic restart following power failure Status LEDs on the front of the housing for quick status recognition LED red for data communication IP over LAN1 LED yellow for data communication MS/TP over RS485-1 LED red for data communication IP over LAN2 LED yellow for data communication MS/TP over RS485-2 LED green as status as soon as the software framework has booted LED blue for power supply on/off BASIC Pre-installed GEZE BASIC configuration software. This allows for integration in other systems, and licence activation for other software applications. Initial access to the device with pre-set fixed IP address and DNS address possible After set-up, the applications can be accessed from a private IP network. Software updates via the software interface VISU Browser-based software application for the visualisation and operation of all connected IO 420 modules. Global event log, scene control per operation or time-control of multiple devices simultaneously. VISU+ Browser-based software application. Displays list of all connected devices, incl. status display. Creation of monitoring functions and specific alarm messages (trigger on particular BACnet objects and their properties) Email reporting service Technical data: ARM processor Clock frequency 1 GHz 512 MB RAM 4 GB eMMC flash memory Supply voltage 24 V DC Max. charging current 250 mA Supply voltage range 24 V+/- 15% Operating range -10 °C to +60 °C IP rating IP20 Housing dimensions 120.4 x 115.8 x 58 cm (W x H x D) |
|  | ......................... pcs. .............................. € .............................. € Planning costs Costs for producing cable diagrams and connection diagrams for individual projects and the preparation of functional descriptions. |
|  | ......................... pcs. .............................. € .............................. € Installation, start-up and official approval Installation, start-up and official approval of the system described with instruction. |
|  | ......................... pcs. .............................. € .............................. € Emergency exit system maintenance service package - compact (standard) Service package for maintenance in accordance with EltVTR (German directive for electrical locking systems on escape route doors) and EN 13637 as well as according to manufacturer’s specifications with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Response time of 24 hours after the fault was reported on workdays (Monday - Friday, 7 am – 5 pm) - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years. |
|  | ......................... pcs. .............................. € .............................. € Emergency exit system maintenance service package - comfort (optional position) Service package for maintenance in accordance with EltVTR (German directive for electrical locking systems on escape route doors) and EN 13637 as well as according to manufacturer’s specifications with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years. |

Safety notes

The safety features of this product are regulated by EltVTR (German directive for electrical locking systems on escape route doors). Modifications and deviations require exemption from the EltVTR. The client must apply for the exemption if necessary.

The emergency push button installed directly next to the door is the most important component of the emergency exit system. If this emergency push button is not included, the door must be activated manually from a permanently occupied desk. This always requires approval by the building authorities responsible.

After activation has been triggered, re-locking can only take place at the door itself. A respective push button (key switch) must be planned on the door for this purpose.

The escape route system may only be fitted to smoke and fire protection doors when proofs of application suitability for these doors include this and their specifications are heeded (EltVTR, section 5).

Installation, cabling and commissioning must be carried out by experts trained by GEZE.